| ABC Petrochemicals Pvt. Ltd. | Document: INC-002 |
| --- | --- |
| Gujarat Manufacturing Plant | Rev: 1.0 ¦ Date: 15-Jan-2026 |

# Control Valve Failure  --  V-220

Equipment: V-220  --  Steam Pressure Control Valve

Incident Date: 18-Feb-2026 | Time: 09:15 hrs

Reported By: Vikram Singh (Shift Lead)

## Incident Description

At 09:15 hrs, the DCS alarmed "Steam Header Pressure High." Investigation revealed control valve V-220 failed to respond to the control signal. The valve was stuck at 45% open while the controller demanded 25%. Downstream pressure rose to 8.2 barg (alarm at 7.5 barg). The emergency steam vent valve (PV-2201) automatically opened at 8.0 barg, preventing a full overpressure event.

## Immediate Actions

Placed V-220 in MANUAL mode  --  position did not respond

Isolated steam supply to valve (bypass valve opened manually)

Actuator air supply checked  --  4.2 barg (within spec)

Scheduled emergency maintenance (WO-2026-0251)

## Root Cause

Valve actuator diaphragm ruptured due to age-related degradation. The actuator was 8 years in service. The diaphragm material (EPDM) showed signs of thermal cracking.

## Corrective Actions

1. Replaced actuator diaphragm (Fisher part no. DIA-220-EPDM-01).

2. Bench-set calibration verified  --  valve strokes 0 - 100% within spec.

3. Added V-220 to critical valve PM schedule with 2-year diaphragm replacement interval.

Reported By: Vikram Singh  |  Reviewed By: Priya Sharma