| ABC Petrochemicals Pvt. Ltd. | Document: INS-003 |
| --- | --- |
| Gujarat Manufacturing Plant | Rev: 1.0 ¦ Date: 15-Jan-2026 |

# Boiler Inspection Report  --  B-101

Equipment: B-101  --  High Pressure Steam Boiler

Inspection Date: 15-May-2026

Inspector: Deepak Joshi (Safety Officer)

## Inspection Scope

Annual external inspection per IBR (Indian Boiler Regulations). Internal inspection deferred to next shutdown.

## External Inspection Findings

Furnace casing  --  no hot spots or bulging detected

Refractory condition  --  minor cracks in burner tile area (noted for repair)

Safety valves (2x)  --  lifting pressure tested at 44 barg and 44.5 barg; reset correctly

Water level gauges  --  clear and operational; blowdown valves functional

Feed water check valve  --  OK, non-return function verified

Insulation  --  intact on drum and headers

## Non-Destructive Testing

UT thickness readings on steam drum (shell):

Bottom: 32.5 mm / 31.8 mm / 32.1 mm (min req'd: 28.0 mm)

Top:   34.2 mm / 33.9 mm / 34.0 mm (min req'd: 28.0 mm)

## Actions Required

1. Repair burner tile refractory during next shutdown.

2. Internal inspection to be completed within 6 months.

Signed: Deepak Joshi  |  Witnessed: Vikram Singh