| ABC Petrochemicals Pvt. Ltd. | Document: MNT-001 |
| --- | --- |
| Gujarat Manufacturing Plant | Rev: 1.0 ¦ Date: 15-Jan-2026 |

# Quarterly Preventive Maintenance  --  Cooling Tower CT-01

Equipment: CT-01  --  Induced Draft Cooling Tower

Date: 05-Apr-2026

Performed By: Suresh Kumar (Maintenance Engineer)

## Work Summary

Routine quarterly preventive maintenance completed on cooling tower CT-01. All six cells inspected.

## Activities Performed

Inspected fan gearbox oil level and condition  --  OK

Greased fan shaft bearings (SKF LGHP 2)

Cleaned and flushed water distribution nozzles

Checked and tensioned V-belts on all 4 fans per cell

Inspected fill media for fouling and scaling

Measured vibration on fan gearbox  --  max 3.2 mm/s

Water treatment chemical dosing verified

Calibrated conductivity controller

## Findings

Cell #3 fill media shows moderate scaling on the hot side. Recommended chemical cleaning during next scheduled turnaround.

## Recommendations

1. Schedule fill media chemical cleaning for Q3 2026.

2. Increase biocide dosing frequency during monsoon months.

## Sign-Off

Maintained By: Suresh Kumar  |  Signature: sk/ct01/05apr26