| ABC Petrochemicals Pvt. Ltd. | Document: MAN-002 |
| --- | --- |
| Gujarat Manufacturing Plant | Rev: 1.0 ¦ Date: 15-Jan-2026 |

# Air Compressor OEM Manual  --  C-201

Equipment: C-201  --  Plant Instrument Air Compressor

Supplier: Atlas Copco (Model: ZR-160)

Compiled By: Suresh Kumar  |  Date: 18-Dec-2025

## 1. General Description

The Atlas Copco ZR-160 is an oil-free rotary screw compressor designed for instrument air supply. It delivers 160 m^3/hr at 8.5 barg with integrated dryer and filtration.

## 2. Specifications

Type: Oil-free rotary screw

Flow: 160 m^3/hr FAD

Pressure: 8.5 barg

Motor: 200 kW, 415V, 3-phase

Cooling: Water-cooled

Dryer: Heatless regenerative

Dew Point: -40 deg C PDP

## 3. Operating Parameters

• Discharge temperature: 85 - 110 deg C (alarm at 120 deg C, trip at 130 deg C)

• Oil pressure: 3.0 - 4.5 barg

• Cooling water inlet: max 32 deg C

• Vibration: < 7.1 mm/s (alert at 11 mm/s)

## 4. Lubrication

Use Atlas Copco Oil Roto-Xtend ND. Oil change interval: 4000 hours. Grease motor bearings every 2000 hours with SKF LGHP 2.

## 5. Safety Devices

• Pressure safety valve set at 10.5 barg

• Motor thermal overload relay

• High discharge temperature trip

• Emergency stop push-button at local panel