| ABC Petrochemicals Pvt. Ltd. | Document: SOP-002 |
| --- | --- |
| Gujarat Manufacturing Plant | Rev: 1.0 ¦ Date: 15-Jan-2026 |

# Centrifugal Pump Shut-Down Procedure

Equipment: P-102  --  Condensate Return Pump (Centrifugal Pump)

Department: Operations

Prepared By: Suresh Kumar  |  Approved By: Rajesh Mehta

## 1. Purpose

To define the safe shut-down sequence for pump P-102 to prevent damage and ensure safe isolation for maintenance.

## 2. Procedure

1. Notify production supervisor before shutdown.

2. Confirm alternate pump is online if continuous operation required.

3. Close discharge valve slowly to 10% to reduce backflow.

4. Press STOP on local control station or DCS.

5. Monitor pump coast-down  --  confirm smooth deceleration.

6. Close discharge valve fully, then close suction valve.

7. Open casing drain valve to relieve internal pressure.

8. Close seal cooling water supply.

9. Apply LOTO on the motor disconnect switch.

10. Record shutdown time and reason in shift log.

## 3. Safety

Hot surfaces  --  allow pump to cool before touching.

Verify LOTO before any maintenance.

Crack drain valve slowly; beware of trapped pressure.