| ABC Petrochemicals Pvt. Ltd. | Document: SOP-003 |
| --- | --- |
| Gujarat Manufacturing Plant | Rev: 1.0 ¦ Date: 15-Jan-2026 |

# Steam Boiler Start-Up Procedure

Equipment: B-101  --  High Pressure Steam Boiler

Department: Operations

Prepared By: Vikram Singh  |  Approved By: Rajesh Mehta

## 1. Purpose

To define the safe start-up sequence for HP steam boiler B-101 to achieve stable combustion and avoid thermal shock.

## 2. Pre-Start Checks

Feed water quality: pH 8.5 - 9.5, conductivity < 10 µS/cm

Fuel gas supply pressure: 2.5 barg

Draft fan and FD fan tested

Gas leak check completed

All safety interlocks functional

## 3. Start-Up Sequence

1. Verify drum water level at 50% (±25 mm) via sight glass.

2. Open superheater vent valve for air purging.

3. Start FD fan; purge furnace for 5 min at >= 30% air flow.

4. Initiate pilot burner ignition; confirm flame scanner detection.

5. Open main fuel gas valve; ramp main burner to 10% load.

6. Increase firing rate max 5%/minute to avoid thermal stress.

7. Close superheater vent at 1 barg drum pressure.

8. Warm steam line by cracking main steam stop valve.

9. Bring boiler to 42 barg at <= 50 deg C/hr heating rate.

10. Place boiler in AUTO mode once stable.

## 4. Safety

Never start without completing furnace purge.

Monitor drum water level constantly.

Adhere to ramp rates to prevent thermal shock.

Two operators must be present during start-up.